## Slide 1: PV potentieel in Nederland & Zonne-energie voorspelling

## Slide 2: Inhoud
Introductie
PV potentieel
PV netwerk integratie
  DNV GL National Smart Grid Model
  Bottom-up aanpak
Conclusies

## Slide 3: Actualiteit

## Slide 4: Introductie
Europese afspraken: 14% duurzame energie in 2020 and 16% in 2023
Op dit moment: ~4% duurzame energie
In 2013 is het Nationaal Energieakkoord gesloten
  Ruim 40 organisaties:
      de overheid, werkgevers, vakbewegingen, natuur- en milieuorganisaties, andere maatschappelijke organisaties en financiële instellingen
  139/159 afspraken zijn “gestart”
Toch zijn er zorgen:
  Bezwaren tegen sluiten kolencentrales
  Onenigheid over bijstoken biomassa
  Verzet tegen windmolens

## Slide 5: Zonne-energie in het Energie akkoord
Energie akkoord:
  Geen specifieke targets zonne-energie
  Zonne-energie onder categorie decentrale duurzame energie
Toch kan zonne-energie een belangrijke bijdrage leveren aan het halen van de doelen:
  Nationaal Actieplan Zonnestroom: 4 GWp in 2020
  Wim Sinke: 4-8 GWp
  ECN: 30 GWp in 2030
Huidige stand:
  > 1 GWp

## Slide 6: Oude potentieelstudies
Potentieelstudies :
  De Noord (2003): 80 – 100 GWp
  Bersma et al (1997): 90 – 110 GWp
  Koot & Middelkoop (2000): 47 GWp
  Alsema & Van Bummelen (1992): 224 GWp
  KPMG (1999): 27 GWp
Meest recente studie: 2003
Hoeveel netwerkcapaciteit?
Chart: Potentieel (GWp)
| 2003 | 1997 | 2000 | 1992 | 1999
Y-Values | 90 | 100 | 47 | 224 | 27

## Slide 7: Inhoud
Introductie
PV potentieel
PV netwerk integratie
  DNV GL National Smart Grid Model
  Bottom-up aanpak
  Lokale case study
Conclusies

## Slide 8: PV Roof Potential
Combining exact building locations with Object Height Register
Calculated tilt and orientation
Corrected average irradiation
Building profiles
Dominant tilt
Orientation
Corrected irradiation

## Slide 9: PV Roof Potential
Corrections for roof edges (4%) and obstacles (36%);
No shadow correction
GIS calculations are very time consuming
Determine available m2 per building type
  Existing residential & commercial buildings on postal code level
  Figure: Available roof area per building type
Notes: Vrijstaand = detached house. Tweekapper = semi-detached

## Slide 10: PV Roof Potential
PV technical details | No irradiation correction | Corrected irradiation
Peak power per m2 | 160 Wp/m2 | 160 Wp/m2
Average peak power production per year | 950 kWh/kWp | 770 kWh/kWp
Average production per m2 | 152 kWh/m2 | 123 kWh/m2
Residential | Commercial | Total
41 GWp | 25 GWp | 66 GWp
32 TWh | 19 TWh | 51 TWh
Roof potential results:
400 km2 potential PV surface
Not included:
PV efficiency increase
Shading by trees and buildings
Infrastructure, ground mounted systems, water, etc.
Notes: PV efficiency will increase to 30-40% resulting to 130 GWp potential.
Shadows from trees or buildings are not included.
Andere toepassingen ook mogelijk: infrastructuur, vrijeveldopstellingen, water.
Verhoging van rendement naar 17% zou betekenen: 66 GWp wordt 70 GWp
Plaatje: verhouding vraag/productie. Donker is hoge productie per huishouden

## Slide 11: Potential in the non-built environment
Locations | Potential
Railways (solar roof & wall) | 6 GWp
Public roads & high ways (roof / wall) | 18 / 6 GWp
Green Houses | 3 GWp
Waste dump sites | 1 GWp
5% of Lake IJssel | > 10 GWp
10% of grass fields | > 50 GWp
160 Wp/m2
770 kWh/kWp

## Slide 12: Inhoud
Introductie
PV potentieel
PV netwerk integratie
  DNV GL National Smart Grid Model
  Bottom-up aanpak
Conclusies

## Slide 13: PV Network Integration - Methodology
DNV GL National Smart Grid Profile Model
  4 Scenarios
  700 MWp (January 2014)
  4 GWp (2020)
  20 GWp (2030)
  150 GWp (thought experiment)
Load flow calculations
Not included:
Voltage analysis (case study)
Network stability and flexibility
Medium Voltage (MV)
High Voltage (HV)
Low Voltage (LV)
HV Generation
HV Consumption
MV Generation
LV Generation
MV Consumption
LV
Consumption

## Slide 14: Construction of the Smart Grid Profile Model
Quantification
Simplified grid model based on limited number of user groups.
Time dependent profiles, partly based on actual weather conditions (Dutch VRJ).
Simplified merit order model based on limited number of central production units types.
scenario’s
# dwellings, utility buildings, penetration PV, HP, CHP, EV etc.
Notes: VRJ: Verkort Referentie Jaar

## Slide 15: Profile approach
Profiles
User Groups
Network
Central Production
Deterministic profiles (EV’s, conventional use)
Meteorological impacted profiles (solar-PV, wind turbines, heat pumps)
Profiles based on control schemes
Volume per user segment
Dimensioning and efficiency of storage
Grid loss parameters
Power per production unit
Efficiencies (H & E)
Investments
Fuel cost
15
Notes: VRJ

## Slide 16
Urban dom. new
Urban dom. existing
Small commercial
Utlity
glastuinbouw
Industry
Renewable
(wind & PV)
Central production
Heavy industry
Inter-connection
Renewable (wind)
HV
LV
Decentralized
Centralized
MV
6
5
8
13
15
16
17
Commercial
Greenhouse cultivation
Industry
12
11
10
18
Rural domestic
7
Shortage/
Surplus
19
9
14
20
grid loss LV:
grid loss MV:
grid loss HV:
Urban dom. new
Urban dom. existing
2
1
Rural domestic
3
Small commercial
4
Local
National
Notes: Wat zijn de rode bollen: punten waar Grid losses berkend worden
‘Local’ gedeelte niet meegenomen in deze studie.

## Slide 17: Power balance - 700 MWp in 2014
Most sunny hour of the year
Notes: Bruin: import/export: meerdere interconnecties die beide kunnen doen. Ook binnen het uur.

## Slide 18: Yearly energy balance - 700 MWp in 2014
PV electricity share: 0,5%

## Slide 19: Power balance – 4 GWp in 2020
Most sunny hour of the year
Notes: Geen probleem bij 4 GWp
Piek rond 3 GWp ivm orientatie, temperatuur en hoek.

## Slide 20: Yearly energy balance – 4 GWp in 2020
PV electricity share: 3%

## Slide 21: Yearly energy balance – 20 GWp in 2030
PV electricity share: 13%
Notes: PV wordt significant in energiebijdrage

## Slide 22: Power balance – 20 GWp in 2030
Most sunny hour of the year
Large export (brown bar, HV cons.)
Notes: Veel export.
Verschil LV prod en LV cons is bijna evengroot/groter dan vraag in winter. Is dit het kantelpunt? Modelheeft altijd een oplossing…

## Slide 23: Power balance – 20 GWp in 2030
Demand response (20%), electric vehicles (50%) & heat pumps (45%)
Less export
Curtailment and storage could bridge the gap between LV production and consumption
Notes: Minder export.
Kleiner gat met LV cons/prod

## Slide 24: The role of storage
Add 2 kWh energy storage for each 5 kWp
This model gives snap shots, energy losses and possibly costs, but not a tripping point
Notes: Low Voltage network is the limiting factor

## Slide 25: Inhoud
Introductie
PV potentieel
PV netwerk integratie
  DNV GL National Smart Grid Model
  Bottom-up aanpak
Conclusies

## Slide 26: What can the network handle? A bottom-up approach
Commercial
40x G
60x H
F
F
F
Commercial
25 x B
25 x C
5 x E
10 x E
5 x A
5 x A
30 x A
5 x B
10 x C
10 x B
12 x C
10 x E
20 x E
MV/LV 630 kVA
District heating
The ‘Meeks grid’ represents a typical Dutch residential community. Our simulations calculate the impact of a scenario on variations of this community
A-D = town house, E-F = detached, G-H = flats, 2 commercials (school, shopping)
Notes: Check de 630 kVA ~ 630 KW transformer

## Slide 27: Approach – “Meeks grid” electric network layout
Simplified layout of the “Meeks grid” electric network
Only two types of grid components considered: transformer (incl. busbars and switches) and cables
MV/LV Transformer
MV grid connection
MV busbar 10 kV
LV busbar 400 V
to Commercial 1
to Block A
to District heating
to Commercial 2
Switches
Cables going into the neighbourhood
to Block B
to Block C
to Block D
to Block E
to Block F
to Flat G
to Flat H
Transformer station

## Slide 28: Results from bottom-up approach
Peak production levelled with peak consumption: 11 GW
Coincidence factor of PV & over dimensioning of transformers: 16 GW
30% curtailment (2-3% energy loss): 23 GW
Temporary transformer overload (few hours/year, 120%): 27 GW
Demand response (0,5 kW per household): +4 GW
‘Conventional’ grid reinforcements: 50 GW
Electricity storage (5 kW per household): +40 GW
Assume homogeneous distribution of PV
Without seasonal energy storage the demand in winter must be provided by other sources
Grid voltage issues will arise (see case study)
Notes: NB: these values reflect real GW, not GWp. In fact GWp could be higher, but this is not calculated. These number are a minimum for GWp

## Slide 29: 150 GWp thought experiment
This scenario will only be plausible if all possible measures are taken:
  E.g. 75% curtailment (35-40% energy loss)
  Grid extensions
  Seasonal storage (hydrogen, thermal acquifiers, power-to-gas, etc)
75% curtailment; 20% DR; 50% HP, EV
75% curtailment; 20% DR; 50% HP, EV, Storage

## Slide 30: Inhoud
Over DNV GL
Introductie
PV potentieel
PV netwerk integratie
  DNV GL National Smart Grid Model
  Bottom-up aanpak
  Lokale case study
Conclusies

## Slide 31: A local case study – a neighbourhood in Arnhem (NL)
Source: Liander, Danny de Pater, 2014

## Slide 32: Coincidence issues production and demand
Source: Liander, Danny de Pater, 2014

## Slide 33: Lessons learned from case study
At maximum PV production the local grid voltage will rise
At maximum load the local grid voltage will drop
The difference between elevated voltage and lowered voltage is limiting the amount of PV and heat pumps.
Exceeding the voltage limits would mean network extension (larger cables and connections)
This induces high social economic costs for a small area: €3000-5000 per household.
Grid operators claim that 1,5 kWp per household is the limit without grid extension (i.e. 33% of electricity demand)
Source: Liander, Danny de Pater, 2014
Notes: 1,5 kWp per household, with 8 million households ~ 12 GWp

## Slide 34: Inhoud
Introductie
PV potentieel
PV netwerk integratie
  DNV GL National Smart Grid Model
  Bottom-up aanpak
Conclusies

## Slide 35: Conclusions
Abundance of roof area
66 GWp with current technology
>150 GWp full potential with all applications
16 GW in present network without measures
(Smart) Grid measures can allow up to 100 GW in the LV grid
Boundary conditions & Limitations
Homogeneous distribution of PV
(Local) voltage issues will appear earlier
Spinning reserve must be provided
Seasonal energy storage is necessary

## Slide 36: Thank you for your attention!
Bas Vet
Bas.Vet@dnvgl.com
+31 (0)26 356 2836